## Over view
Water Operators Report Aug 2022
Prepared by: Dave Shepherd
Water consumption
Monthly Consumption |  | 19259 | M3 | 28 | 687.8214 | M3 | Daily Average
Previous year 2021-01 |  | 16105 | M3 | 28 | 575.1786 | M3 | Daily Average
19.58%
Vol Well #1 since 19 Jan 2019 |  | 233.13 | M3
Max Flow for month |  | 1579.3 | L/Min | Min Flow for month |  | 150.5 | L/Min (leak rate)
Time and Date |  | 06/08/2022 06:44 |  |  | 12/08/2022 13:15
Pump hours |  | # 2 | 669 | # 3 | 283 | #4 | 407
Previous month hrs |  |  | 671 |  | 160 |  | 522
VIHA Samples
Activity | Date | Location |  | Sample type | Result
Monthly | 08/08/2022 | 7941 Park |  | Drinking water | ü | Sent to VIHA
Sample /testing |  | 7588 Ships Pt. |  | Drinking water | ü
|  | 7576 Tozer |  | Drinking water | ü
|  | Well 2 |  | Raw | ü
|  | Well 3 |  | Raw | ü
|  | Well 4 |  | Raw | ü
Operations/Maintenance
Weekly:
Meter readings, CL residuals (5 locations) incl flushing station, run pump 1 collect well levels data
Check CL tank level and add accordingly
Monthly:
Prep chain of custody report and sample bottles Collect VIHA samples and deliver to office
Collect end of month Data create report, replace CL membrane, order chlorine as needed
Attend WTC and SPID Meetings
05/08/2022 | Calibrate Pump house CL meter with BWS meter pH now reading 7.1 with #2 and #3 combined
(was 6.7) add BWS well level sensor in #4 along side existing MM to graph results
17/08/2022 | Jim W Mike M and Dave S met with Grant Cyz and Co. from "Kirnel" water district (Denman)
They are in the investigation phase of improving their small system (20 connections)
24/08/2022 | Measure up Pump house to Shed 1 and 2 for wild fire sprinkler protection
Recommend purchase a "smart Valve" as a part of the system so can be operated manually or
remotley via phone app. In case operators fighting fires
To cover Control building, shed 1 and wells 2,3 and 4 with wild fire protection sprinklers Est 500.00